STANDARD OPERATING PROCEDURE

Replacing an Industrial Temperature Sensor

Document No. SOP-INST-014   |   Revision C   |   Effective Date: 2026-07-29

# 1. Purpose

This procedure describes the safe and consistent method for removing a failed or out-of-calibration industrial temperature sensor (RTD or thermocouple) from a process thermowell and installing a replacement, so that process measurement is restored with minimal downtime and without compromising personnel safety or process integrity.

This procedure applies to temperature sensors installed in thermowells on piping, vessels, and equipment within the facility's process areas. It does not cover thermowell replacement, transmitter programming from a blank/uncommissioned state, or hazardous-area sensor types requiring specialized intrinsic-safety documentation — refer to the relevant equipment-specific procedures for those tasks.

# 2. Required Personal Protective Equipment (PPE)

- Safety glasses with side shields (face shield if process temperature exceeds 150°C / 300°F or line is pressurized)

- Heat-resistant gloves rated for the process temperature; nitrile gloves for chemical contact where applicable

- Steel-toed safety footwear

- Flame-resistant (FR) coveralls in designated process units

- Hearing protection where required by area posting

- Hard hat in designated overhead-hazard zones

# 3. Required Tools and Materials

- Replacement temperature sensor matching the original specification (type, range, sheath diameter, insertion length, connection head style)

- Calibrated multimeter (resistance/continuity capable)

- Adjustable and open-end wrenches sized for the connection head and compression fitting

- Torque wrench with appropriate socket/crowfoot for fitting torque spec

- Wire strippers and terminal screwdriver set

- Replacement gasket or ferrule (if compression/flanged fitting)

- Thermal transfer compound (approved for process temperature)

- Lockout/tagout (LOTO) kit and personal lock

- Portable gas detector (for hydrocarbon or other hazardous-atmosphere areas)

- Loop diagram / instrument data sheet for the tag being serviced

- Permit-to-work / hot work permit, if required by area classification

# 4. Safety Precautions

- Do not begin work until a valid work permit (and hot work / confined space permit if applicable) has been issued and reviewed.

- Apply lockout/tagout on the associated control loop and any automated valves affected by the sensor signal; verify zero energy state before opening the instrument.

- Confirm the process line or vessel has been isolated, depressurized, and cooled to a safe handling temperature before removing the sensor from the thermowell. Never remove a sensor from a thermowell that is still in an energized, pressurized, or hot process.

- Verify the thermowell itself is not being removed — only the sensor element. Removing a thermowell under pressure is a serious hazard and is outside the scope of this procedure.

- Check the area classification (hazardous location rating) and confirm the replacement sensor and any temporary test equipment are rated for that classification.

- Use a gas detector before and during work in areas with potential hydrocarbon or toxic gas release.

- Support the sensor and cabling during removal to avoid strain on adjacent conduit, cable tray, or junction boxes.

- Never bypass or defeat a safety instrumented function (SIF) associated with this measurement without following the facility's management of change (MOC) and bypass authorization process.

- If the sensor failure is associated with a process upset or safety event, do not disturb the sensor until released by the incident investigation team.

# 5. Step-by-Step Instructions

- Review documentation. Pull the instrument tag's loop diagram, data sheet, and last calibration record. Confirm the replacement sensor matches specification (type, range, sheath length, connection style).

- Obtain permits and isolate. Obtain the work permit. Place the control loop in manual/bypass per the MOC-approved method, apply LOTO to the circuit, and verify zero energy with a calibrated meter.

- Verify process isolation. Confirm the associated line or vessel is isolated, depressurized, and at a safe handling temperature. Check with a non-contact thermometer if unsure.

- Notify control room. Inform the control room / operations that the instrument is being taken out of service and confirm any alarms or interlocks tied to this tag are acknowledged or bypassed per MOC.

- Disconnect wiring. Open the connection head cover. Photograph or note terminal wiring, then disconnect leads from the terminal block. Cap or tape wire ends.

- Remove the sensor. Loosen the compression fitting or union nut at the thermowell and withdraw the sensor element straight out, avoiding bending the sheath.

- Inspect the thermowell. Check the thermowell bore for debris, corrosion, or damage. Clean if necessary. Do not proceed if the thermowell itself shows cracking, wall thinning, or damage — escalate for thermowell replacement.

- Apply thermal compound. Apply a thin, even layer of approved thermal transfer compound to the sensing tip of the new sensor per manufacturer instructions.

- Insert the new sensor. Insert the replacement sensor to the full specified insertion depth so the tip seats at the bottom of the thermowell bore.

- Torque the fitting. Tighten the compression fitting or union nut to the specified torque in a star pattern where multiple bolts are present. Do not overtighten.

- Reconnect wiring. Land the leads on the terminal block per the loop diagram, matching polarity for RTDs (2/3/4-wire) or thermocouple leg polarity. Verify tightness of each terminal.

- Close the connection head. Reinstall the connection head cover, ensuring any gasket seats correctly for the housing's ingress protection rating.

- Bench/loop check. With the loop still isolated from automatic control, verify sensor resistance or millivolt output at the terminal block with a multimeter and compare to expected values at ambient temperature.

- Remove LOTO and restore. Once verified, remove personal locks per procedure, restore power to the loop, and return the loop to automatic control per MOC.

- Verify reading in the DCS/PLC. Confirm the displayed process value is reasonable and stable, and matches a reference measurement if available.

- Close out documentation. Update the instrument's maintenance record, close the work permit, and file the calibration/replacement record.

# 6. Inspection Checklist

Complete before returning the loop to automatic control:

- Replacement sensor matches tag specification (type, range, length, connection style)

- Thermowell bore inspected — clean, no cracking or damage

- Thermal transfer compound applied to sensor tip

- Sensor inserted to full specified depth

- Fitting torqued to specification; no visible leak path

- Wiring polarity and terminal assignment verified against loop diagram

- All terminals mechanically tight

- Connection head cover reinstalled and sealed

- Bench check value reasonable at ambient temperature

- LOTO removed only after verification complete

- DCS/PLC reading confirmed stable and reasonable

- Work permit closed and maintenance record updated

# 7. Troubleshooting

If the loop does not behave as expected after installation, use the table below before re-opening the connection head.

| Symptom | Probable Cause | Corrective Action |
| --- | --- | --- |
| No signal / open circuit reading after replacement | Loose or miswired terminal connection; broken lead wire | Verify wiring against the loop diagram; check terminal torque; inspect leads for damage; confirm continuity with a multimeter. |
| Reading is erratic or noisy | Damaged signal cable, poor shield grounding, or nearby EMI source (VFD, contactor) | Inspect cable shield termination (ground at one end only); reroute cable away from power conductors; replace damaged cable. |
| Reading is stable but inaccurate compared to reference | Incorrect sensor type/range programmed at the transmitter or DCS; poor thermal contact with the process | Confirm sensor type (RTD/TC) and range configuration matches the new sensor; verify immersion depth and thermowell contact; re-calibrate transmitter. |
| Sensor reads process temperature slowly | Air gap in thermowell; missing thermal compound; insufficient insertion length | Remove sensor, apply approved thermal transfer compound, reinsert to full specified depth, and re-torque. |
| Leak at thermowell or fitting after reinstallation | Damaged gasket/ferrule, incorrect torque, or cross-threading | De-energize/depressurize per LOTO, replace gasket or ferrule, re-torque to spec in a star pattern, and re-test. |
| Alarm or trip on startup | Transmitter configuration not restored, or sensor polarity reversed (RTD 3-wire) | Verify wiring polarity and terminal assignment; reload/verify transmitter configuration against the loop record before returning to service. |

# 8. Revision History

| Rev. | Date | Author | Description of Change |
| --- | --- | --- | --- |
| A | 2025-03-10 | M. Reyes, Maint. Eng. | Initial release. |
| B | 2025-09-02 | M. Reyes, Maint. Eng. | Added lockout/tagout verification step and updated torque spec for compression fittings. |
| C | 2026-07-29 | Document Control | Reformatted to current SOP template; added troubleshooting section. |